Recommended Specifications for Areo-Power Fireguard Tanks

for New York City

A.	General

The above-ground storage tank system shall be as manufactured by Areo-Power Unitized Fueler, Inc., and as shown on tank construction drawing number ________.

The unit shall consist of a _______ type I double wall inner tank with dished heads.  This assembly shall be contained by a type II wrap and thermally insulated to FireguardTM  specifications  The horizontal cylindrical storage tank  shall be mounted on saddles within a containment dike providing secondary containment of at least 110% of primary tank capacity.

The tank shall be a UL2085 listed by Underwriters Laboratories, Inc. (UL) and labeled with the UL "Insulated Secondary Containment Aboveground Tank for Flammable Liquids" label.

# B.	Materials

- The tank, dike and all steel appurtenances shall be fabricated from commercial or structural grade carbon steel.  Only new materials shall be used.

- All carbon steel shall comply with the latest edition of the Specification for Structural Steel, ASTM A36; or the Specification for Steel, Carbon (0.15 Maximum, Percent), Hot Rolled Sheet and Strip, Commercial Quality, ASTM A569.

- Insulating material shall be lightweight and porous to allow for leak migration to a leak monitoring point.  The insulation material shall be as specified by the Steel Tank Institutes Standard for FireguardTM Tanks and shall have an R factor of 10.

C.	Size and Dimensions

- The primary tank shall be ______ diameter by ___  long.  The shell steel thickness shall be ____ and tank heads shall be ____.  The outer shell of the double wall tank shall be 12" larger in diameter and length, giving a 6"annular space for lightweight insulation material.

- The containment dike shall be _____ wide by ____ long by _____ high.  The containment dike steel thickness shall be _____.

D.	Primary Tank Fittings

- All fittings will be sized and located as indicated on the tank construction drawing.

- All fittings shall be protected with plastic thread protectors to prevent damage to threads and minimize foreign matter from entering the tank during shipping.

E.	Assembly and Appurtenances

- The “triple wall” tank shall be furnished with 3" high saddle supports.

- The containment dike shall be furnished with support dunnage to allow for visual inspection of containment dike bottom.  The size and location of supports shall be as indicated on the tank construction drawing.

- The unit will be provided with a drip pan type pump platform of the size and location indicated on the tank drawing.

- The unit shall be provided with removable 12 ga. (min) steel rainshields designed to minimize water and debris from entering the diked area.  The rainshield design will allow for easy visual interior dike inspection while allowing the dike area to be naturally ventilated to avoid possible vapor collection.

- The lightweight insulation material shall not be exposed to weathering and shall be completely protected from damage between two steel walls of the “triple” wall tank.

- The tank shall be provided with a fill containment sump designed to contain spills of up to 3 gal.(approximately) in a tank top reservoir while a 1" sch 40 overflow pipe diverts spills in excess of 3 gal in to the containment dike.

- The inner tank, tank wrap and outer tank shall be furnished with _____ emergency vents designed to relieve internal tank pressure in excess of  0.5 psig.  The emergency vent shall have a _______ cubic feet per hour (cfh) rating at 2.5 psig.

- The tank assembly shall be provide with an emergency vent protection hood designed to prevent snow, ice and debris from rendering the emergency vent ineffective while allowing the vent to operate as intended.  The hood shall provide a cross sectional venting area of 160 square inches.

- An emergency vent diverter shall be provided such that under emergency conditions the first 9 gallons (approximately) of product emitted from the emergency vent will be contained in a tank top reservoir using a weir plate.  Emissions in excess of 9 gallons shall be directed to the containment dike via a chute of rectangular cross section having an area of 48 square inches.

- The containment dike shall be provided with a sump and 3/4" sch 40 drawoff pipe to allow liquid to be pumped out of the dike.

- The unit will be provided with stairs, landing and handrails designed in accordance with OSHA requirements.  The top of the staircase shall attach to the front head of the tank to allow easy tank top filling.  The stair frame and handrails shall be fabricated from carbon steel.  Stair treads and fill platforms shall be constructed of slip resistant grating.

- The tank and dike shall be provided with separate lifting lugs such that the tank and dike may be lifted separately.

F.	Exterior Coating for Steel Parts

- All exterior steel surfaces (including the interior of the containment dike) shall be factory grit blasted to the Steel Structures Paint Councils Surface Preparation Specification No. 7 (SSPC-SP7) and coated with the manufactures standard white finish (epoxy, polyurethane, enamel at manufacturers option).

G.	Factory Testing Requirements

- The tank shall be factory tested in accordance with the requirements of UL2085.  Additionally the primary tank shall be tested hydrostatically to a pressure of 30 psig.